## Inputs & BOM
115 kWp commercial rooftop, Islamabad: inputs and bill of materials
Demonstration project. Yellow cells are inputs; everything else is a formula. Module and inverter figures from the Jinko and Huawei datasheets; PKR rates are illustrative.
| Inputs | [5 empty] | Design check
| Module power (W) | 580 |  |  |  |  | Total modules |  | 198
| Module Voc (V) | 52.31 |  |  |  |  | DC capacity (kWp) |  | 114.84
| Voc temperature coefficient (%/C) | -0.25 |  |  |  |  | Module Voc on the coldest morning (V) |  | 56.2332
| Lowest temperature on site (C) | -5 |  |  |  |  | String Voc on the coldest morning (V) |  | 1012.1985
| Modules per string | 18 |  |  |  |  | Voltage check |  | OK
| Number of strings | 11 |  |  |  |  | Row length (m) |  | 20.772
| Inverter max DC voltage (V) | 1100
| Module width plus gap (m) | 1.154
Bill of materials
Line | Item | Category | Unit | Qty | Unit rate (PKR) | Budget (PKR) | Supplier | Lead time (days) | Needed for
1 | PV module, Jinko JKM580N-72HL4-V 580 W | Modules | pcs | 198 | 15660 | 3100680 | Module distributor | 8 | Module installation start
2 | Inverter, Huawei SUN2000-100KTL-M2 | Inverter and monitoring | pcs | 1 | 1450000 | 1450000 | Inverter distributor | 12 | Electrical installation start
3 | Monitoring dongle (4G) | Inverter and monitoring | pcs | 1 | 42000 | 42000 | Inverter distributor | 12 | Electrical installation start
4 | Mounting rail, 4.2 m | Mounting | pcs | 110 | 4800 | 528000 | Mounting supplier | 7 | Mounting installation start
5 | Module clamps (mid and end) | Mounting | pcs | 418 | 220 | 91960 | Mounting supplier | 7 | Mounting installation start
6 | Roof attachment (L-foot with fixings) | Mounting | pcs | 418 | 450 | 188100 | Mounting supplier | 7 | Mounting installation start
7 | DC solar cable 6 mm2 (red and black) | DC electrical | m | 968 | 260 | 251680 | Electrical wholesaler | 4 | Module installation start
8 | MC4 connector pair | DC electrical | pairs | 25 | 350 | 8750 | Electrical wholesaler | 4 | Module installation start
9 | Cable tray, galvanised | DC electrical | m | 60 | 1800 | 108000 | Electrical wholesaler | 5 | Electrical installation start
10 | AC cable, 4-core 70 mm2 Cu armoured | AC electrical | m | 33 | 8500 | 280500 | Electrical wholesaler | 6 | Electrical installation start
11 | MCCB 4-pole 200 A | AC electrical | pcs | 1 | 85000 | 85000 | Electrical wholesaler | 7 | Electrical installation start
12 | Surge protection device, Type 2 | AC electrical | pcs | 1 | 28000 | 28000 | Electrical wholesaler | 7 | Electrical installation start
13 | Earthing (2 earth pits and 60 m cable) | Earthing | lot | 1 | 104000 | 104000 | Electrical wholesaler | 3 | Mounting installation start
14 | Installation crew | Labour and services | crew-days | 5 | 30000 | 150000 | Installation subcontractor | 5 | Mounting installation start
15 | Electrical crew | Labour and services | crew-days | 4 | 35000 | 140000 | Installation subcontractor | 5 | Electrical installation start
16 | Transport and lifting | Labour and services | lot | 1 | 150000 | 150000 | Logistics provider | 3 | Mobilisation
17 | Access and safety equipment | Labour and services | lot | 1 | 80000 | 80000 | In-house | 5 | Mobilisation
18 | Testing and commissioning | Labour and services | lot | 1 | 120000 | 120000 | In-house | 5 | Testing and commissioning
19 | Net-metering application and meter | Approvals | lot | 1 | 200000 | 200000 | DISCO | 35 | Net-metering energisation
| Total budget |  |  |  |  | 7106670

## Procurement
Procurement tracker
Order by = the date it is needed on site, minus the lead time and a buffer, counting Monday to Saturday as working days.
Project dates
| Contract award date | 2026-09-07
| Status date (today in this example) | 2026-09-21
| Ordering buffer (days) | 3
Programme milestones
| Milestone | Working days after award | Date
| Contract award | 0 | 2026-09-07
| Mobilisation | 14 | 2026-09-23
| Mounting installation start | 15 | 2026-09-24
| Module installation start | 19 | 2026-09-29
| Electrical installation start | 21 | 2026-10-01
| Testing and commissioning | 26 | 2026-10-07
| Net-metering energisation | 45 | 2026-10-29
Purchase orders
Line | Item | Needed for | Required on site | Lead time (days) | Order by | PO date | Expected delivery | Delivered | Days in hand | Status
1 | PV module, Jinko JKM580N-72HL4-V 580 W | Module installation start | 2026-09-29 | 8 | 2026-09-16 | 2026-09-15 | 2026-09-24 |  | 5 | On order
2 | Inverter, Huawei SUN2000-100KTL-M2 | Electrical installation start | 2026-10-01 | 12 | 2026-09-14 | 2026-09-18 | 2026-10-02 |  | -1 | Late delivery
3 | Monitoring dongle (4G) | Electrical installation start | 2026-10-01 | 12 | 2026-09-14 | 2026-09-18 | 2026-10-02 |  | -1 | Late delivery
4 | Mounting rail, 4.2 m | Mounting installation start | 2026-09-24 | 7 | 2026-09-12 | 2026-09-11 | 2026-09-19 | 2026-09-19 | 5 | Delivered
5 | Module clamps (mid and end) | Mounting installation start | 2026-09-24 | 7 | 2026-09-12 | 2026-09-11 | 2026-09-19 | 2026-09-19 | 5 | Delivered
6 | Roof attachment (L-foot with fixings) | Mounting installation start | 2026-09-24 | 7 | 2026-09-12 | 2026-09-11 | 2026-09-19 | 2026-09-19 | 5 | Delivered
7 | DC solar cable 6 mm2 (red and black) | Module installation start | 2026-09-29 | 4 | 2026-09-21 |  |  |  | 0 | Order due
8 | MC4 connector pair | Module installation start | 2026-09-29 | 4 | 2026-09-21 |  |  |  | 0 | Order due
9 | Cable tray, galvanised | Electrical installation start | 2026-10-01 | 5 | 2026-09-22 |  |  |  | 1 | Order due
10 | AC cable, 4-core 70 mm2 Cu armoured | Electrical installation start | 2026-10-01 | 6 | 2026-09-21 | 2026-09-19 | 2026-09-26 |  | 5 | On order
11 | MCCB 4-pole 200 A | Electrical installation start | 2026-10-01 | 7 | 2026-09-19 |  |  |  | -2 | Order overdue
12 | Surge protection device, Type 2 | Electrical installation start | 2026-10-01 | 7 | 2026-09-19 | 2026-09-18 | 2026-09-26 |  | 5 | On order
13 | Earthing (2 earth pits and 60 m cable) | Mounting installation start | 2026-09-24 | 3 | 2026-09-17 | 2026-09-16 | 2026-09-19 | 2026-09-19 | 5 | Delivered
14 | Installation crew | Mounting installation start | 2026-09-24 | 5 | 2026-09-15 | 2026-09-14 | 2026-09-19 |  | 5 | On order
15 | Electrical crew | Electrical installation start | 2026-10-01 | 5 | 2026-09-22 |  |  |  | 1 | Order due
16 | Transport and lifting | Mobilisation | 2026-09-23 | 3 | 2026-09-16 | 2026-09-15 | 2026-09-18 |  | 5 | On order
17 | Access and safety equipment | Mobilisation | 2026-09-23 | 5 | 2026-09-14 | 2026-09-12 | 2026-09-18 | 2026-09-18 | 5 | Delivered
18 | Testing and commissioning | Testing and commissioning | 2026-10-07 | 5 | 2026-09-28 |  |  |  | 7 | Not yet due
19 | Net-metering application and meter | Net-metering energisation | 2026-10-29 | 35 | 2026-09-15 | 2026-09-10 | 2026-10-21 |  | 8 | On order
Formulas:
Date = WORKDAY.INTL(D5,tblMilestones[[#This Row],[Working days after award]],11)
Date = XLOOKUP(tblProc[[#This Row],[Needed for]],tblMilestones[Milestone],tblMilestones[Date])
Order by = WORKDAY.INTL(tblProc[[#This Row],[Required on site]],-(tblProc[[#This Row],[Lead time (days)]]+D7),11)
Expected delivery = IF(tblProc[[#This Row],[PO date]]="","",WORKDAY.INTL(tblProc[[#This Row],[PO date]],tblProc[[#This Row],[Lead time (days)]],11))

## Cost
Cost tracker: budget, committed and forecast
Committed = value of purchase orders placed. Forecast = committed if there is a PO, otherwise the budget. Variance = budget minus forecast (negative is over budget).
By BOM line | [7 empty] | By category
Line | Item | Category | Budget (PKR) | Committed (PKR) | Forecast (PKR) | Variance (PKR) | Variance % | Category | Budget | Committed | Forecast | Variance
1 | PV module, Jinko JKM580N-72HL4-V 580 W | Modules | 3100680 | 3100680 | 3100680 | 0 | 0% | Modules | 3100680 | 3100680 | 3100680 | 0
2 | Inverter, Huawei SUN2000-100KTL-M2 | Inverter and monitoring | 1450000 | 1450000 | 1450000 | 0 | 0% | Inverter and monitoring | 1492000 | 1492000 | 1492000 | 0
3 | Monitoring dongle (4G) | Inverter and monitoring | 42000 | 42000 | 42000 | 0 | 0% | Mounting | 808060 | 856600 | 856600 | -48540
4 | Mounting rail, 4.2 m | Mounting | 528000 | 559700 | 559700 | -31700 | -6.004% | DC electrical | 368430 | 0 | 368430 | 0
5 | Module clamps (mid and end) | Mounting | 91960 | 97500 | 97500 | -5540 | -6.024% | AC electrical | 393500 | 297300 | 382300 | 11200
6 | Roof attachment (L-foot with fixings) | Mounting | 188100 | 199400 | 199400 | -11300 | -6.007% | Earthing | 104000 | 104000 | 104000 | 0
7 | DC solar cable 6 mm2 (red and black) | DC electrical | 251680 | 0 | 251680 | 0 | 0% | Labour and services | 640000 | 380000 | 640000 | 0
8 | MC4 connector pair | DC electrical | 8750 | 0 | 8750 | 0 | 0% | Approvals | 200000 | 200000 | 200000 | 0
9 | Cable tray, galvanised | DC electrical | 108000 | 0 | 108000 | 0 | 0% | Total | 7106670 | 6430580 | 7144010 | -37340
10 | AC cable, 4-core 70 mm2 Cu armoured | AC electrical | 280500 | 269300 | 269300 | 11200 | 3.993%
11 | MCCB 4-pole 200 A | AC electrical | 85000 | 0 | 85000 | 0 | 0%
12 | Surge protection device, Type 2 | AC electrical | 28000 | 28000 | 28000 | 0 | 0%
13 | Earthing (2 earth pits and 60 m cable) | Earthing | 104000 | 104000 | 104000 | 0 | 0%
14 | Installation crew | Labour and services | 150000 | 150000 | 150000 | 0 | 0%
15 | Electrical crew | Labour and services | 140000 | 0 | 140000 | 0 | 0%
16 | Transport and lifting | Labour and services | 150000 | 150000 | 150000 | 0 | 0%
17 | Access and safety equipment | Labour and services | 80000 | 80000 | 80000 | 0 | 0%
18 | Testing and commissioning | Labour and services | 120000 | 0 | 120000 | 0 | 0%
19 | Net-metering application and meter | Approvals | 200000 | 200000 | 200000 | 0 | 0%
| Total |  | 7106670 | 6430580 | 7144010 | -37340

## Dashboard
115 kWp commercial rooftop: project dashboard
Status date 21 Sept 2026. Demonstration project with illustrative PKR rates.
DC CAPACITY |  | BUDGET | FORECAST | PROCUREMENT
114.84 |  | 7106670 | 7144010 | 3 late or overdue
Voltage check: OK |  | PKR 61.9 per Wp | PKR 37,340 over budget | 4 to order within 3 days
Lines by status
[5 empty] | Status | Lines
[5 empty] | Delivered | 5
[5 empty] | On order | 6
[5 empty] | Order due | 4
[5 empty] | Not yet due | 1
[5 empty] | Late delivery | 2
[5 empty] | Order overdue | 1
[5 empty] | Total | 19
PivotTable: budget by category (filter with the Supplier slicer)
Category | Budget (PKR)
Modules | 3100680
Inverter and monitoring | 1492000
Mounting | 808060
Labour and services | 640000
AC electrical | 393500
DC electrical | 368430
Approvals | 200000
Earthing | 104000
Grand Total | 7106670
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.